## Power Consumption
Appliance – Watts | Appliance – Watts | Appliance – Watts
Coffee pot – 200 | Garage door opener – 350 | Compact Fluorescent (CF)
vs. Incandescent Wattage*
Coffee maker – 800 | Ceiling fan – 10-50
Toaster – 800-1500 | Table fan – 10-25 | 40 watt incan. – 11 watt CF
Popcorn popper – 250 | Electric blanket – 200 | 60 watt incan. – 16 watt CF
Blender – 300 | Blow dryer – 1000 | 75 watt incan. – 20 watt CF
Microwave – 600-1500 | Shaver – 15 | 100 watt incan. – 30 watt CF
Waffle iron – 1200 | Water Pik – 100 | Hedge trimmer – 450
Hot plate – 1200 | Computer… | Weed eater – 500
Frying pan – 1200 | laptop – 20-50 | 1/4" drill – 250
Dishwaher – 1200-1500 | desktop – 80-150 | 1/2" drill – 750
Gbg. disposal – 450 | printer – 100 | 1" drill – 1000
Washing machine… | Typewriter – 80-200 | 9" disc sander – 1200
automatic – 500 | TV (25" color) – 150 | 3" belt sander – 1000
manual – 300 | TV (19" color) – 70 | 12" chain saw – 1100
Vaccuum… | TV (12" B&W) – 20 | 14" band saw – 1100
upright – 200-700 | VCR – 40 | 7 1/4" circ. saw – 900
handheld – 100 | CD player – 35 | 8 1/4" circ. saw – 1400
Sewing Machine – 100 | Portable stereo – 10-30 | Refrig./Freezer – Conventional…
Iron – 1000 | Clock radio – 1 | 20 cubic feet – 540
Clothes dryer… | Car stereo – 8 | 16 cubic feet – 475
electric (n/a) – 4000 | Sattelite dish – 30 | Sun Frost Refrig./Freezer (DC*)…
gas heated – 300-400 | CB radio – 5 | 16 cubic feet – 112
Heater (n/a)… | Electric clock – 3 | 12 cubic feet – 70
engine block – 150-1000 | Radio telephone… | Vestfrost Refrig./Freezer…
portable – 1500 | receive – 5 | 10.5 cubic feet – 60
waterbed – 400 | transmit – 40-150 | Freezer – Conventional…
stock tank – 100 | Lights… | 14 cubic feet FF – 440
Furnace blower – 300-1000 | 100w incan. – 100 | 14 cubic feet – 350
Air Conditioner (n/a)… | 25w CF – 28 | Sun Frost Freezer (DC)…
room – 1000 | 50w DC incan. – 50 | 19 cubic feet – 112
central – 2000-5000 | 40w DC halogen – 40 | Vestfrost Freezer…
Electric mower (n/a) – 1500 | 20w CF – 22 | 7.5 cubic feet – 50

## Sizing Load Form-Res
|  | Worksheet - NEC 2011, 220 Part IV | [5 empty] | Residential
Customer Name
Customer Address | [6 empty] | email:
Phone
Date | [6 empty] | Fax:
Voltage (Circle) |  | 120/240V- 1Ø |  | 120V/208Y - 3Ø |  |  | 120V/240Δ - 3Ø
Electrical Service (Circle) | 100 Amp |  | 150 Amp | 200 Amp | 400 Amp |  | 800 Amp |  | NJ Elctrical License
Fuel Type (Circle) |  |  | LPV | NG |  |  |  |  | NJ HIC# 13VH
Panel Loc/Distance to Gen Loc |  | Garage | Basement | Room | Dist._______ |  | Ft. | PrePack | Whole-House
General Loads | Sq.Ft | Qty. | Rating | Factor | Loads (VA) |  |  |  | Loads(VA) kW(VA/1000) |  | Amps
General Lighting |  |  | 3VA per ft² | 100% | 0 |  |  | 0 |  |  | 0
Small Appliance Circuits |  |  | 1500 | 100% | 0 |  |  | 0 |  |  | 0
Laundry Circuits |  | 0 | 1500 | 100% | 0 |  |  | 0 |  |  | 0
Fixed Appliances |  |  | Full Power Rating |  |  |  |  | Gen kW Rating |  |  | Full Current Rating
Well Pump | 230V |  | 1000 | 100% | 0 | VA | 1 | 0 | kW | 4.2 | 0 | A
Sump Pump | 120V | 0 | 750 | 100% | 0 |  | 0.75 | 0 |  | 5.5 | 0
Ejector Pump 1 h.p. | 230V | 0 | 2000 | 100% | 0 |  | 2 | 0 |  | 7.5 | 0
Freezer | 120V | 0 | 400 | 100% | 0 |  | 0.4 | 0 |  | 3.3 | 0
Microwave | 120V | 0 | 1000 | 100% | 0 |  | 1 | 0 |  | 8.3 | 0
Toaster Oven | 120V | 0 | 1250 | 100% | 0 |  | 1.25 | 0 |  | 10 | 0
Disposal | 120V | 0 | 250 | 100% | 0 |  | 0.25 | 0 |  | 2 | 0
Dishwasher | 120V | 0 | 500 | 100% | 0 |  | 0.5 | 0 |  | 4.5 | 0
Range (See Table 220.55 for Multiple Cooking App. Or per 8" Element | 230V | 0 | 1500 | 100% | 0 |  | 1.5 | 0 |  | 6.3 | 0
Wall Mounted Oven | 230V | 0 | 5000 | 100% | 0 |  | 5 | 0 |  | 25 | 0
Water Heater (Electric) | 230V | 0 | 4500 | 100% | 0 |  | 4.5 | 0 |  | 18.5 | 0
Clothes Dryer (Electric) | 230V | 0 | 5000 | 100% | 0 |  | 5 | 0 |  | 21 | 0
Furnace/Air Handler | 120V | 0 | 750 | 100% | 0 |  | 0.75 | 0 |  | 7 | 0
Refrigerator | 120V | 0 | 750 | 100% | 0 |  | 0.75 | 0 |  | 6 | 0
Other(s) List |  | 0 |  |  |  |  | 0
|  | 0 |  |  |  |  | 0
Total Special Loads |  |  |  |  | 0 | VA |  | 0 | kW |  | 0 | A
Heat / AC Loads |  | Qty. | Rating | Factor | Loads (VA) |  |  |  | Loads(VA) kW(VA/1000) |  | Amps
AC Cooling Equipment |  |  | Ton |  |  | Locked-Rotor Amp(LRA) |  | Gen kW Rating |  | Running Load Amp(RLA)
• Compressor 1 | 230V | 0 | 0 | 100% | 0 |  | 0 | 0 |  | 0 | 0 | A
• Compressor 2 | 230V | 0 | 0 | 100% | 0 |  | 0 | 0 |  | 0 | 0
• Heating Element | 230V | 0 |  | 100% |  |  |  | 0
• Heat Pump | 230V | 0 |  | 100% |  |  |  | 0
Electric Space Heating
• Less than 4 separately controlled units |  | 0 | 0 | 100% | 0 |  |  | 0 |  | 0 | 0
• 4 or more separately controlled units |  | 0 | [5 empty] | 0
Any Continuous Nameplate Load |  | 0 | [5 empty] | 0
Total AC/Heat Loads |  |  |  |  | 0 | VA |  | 0 | kW |  | 0 | A
General Loads | [9 empty] | Total A | 0 | A
• 1st 10kW of General Loads |  |  |  | 100% | 0 | kW
• Remaining General Loads (kW) |  |  |  | 40% | 0 | kW
Calculated General Loads (kW) | [7 empty] | 0 | kW |  | 0 | A
AC Load |  |  |  | 100% | 0
Heat Load |  |  |  | 100% | 0
Largest of AC/Heat Load | [7 empty] | 0 | kW |  | 0 | A
Total Calculated Load (Net General Loads + Heat/AC Loads) |  |  |  |  | 0 | VA |  | 0 | kW |  | 0 | A
| Actual Generator size = Total x 10% |  |  |  | 0 | kW |  | 0 | kW | * *
*Whole-House: Use as is. |  |  |  |  | 8/7kW = 35amps (28-amp max after adding up items)
*When doing partial-building, look at the amp total (Total A). Than look at |  |  |  |  | 10/9kW = 45amps (36-amp max after adding up items)
the Amp/CB table to the right. This is more accurate due to all the items |  |  |  |  | 14/13kW = 60amps (48-amp max after adding up items)
selected are likely to be on at same time. |  |  |  |  | 17/16kW = 65amps (52-amp max after adding up items)
20/18kW = 100amp (80-amp max after adding up items)
|  |  | Yellow = Entry |  | If used as whole-house, follow sheets recommendation
Use forPartial Building
}

## Sizing Load Form-Comm
Commercial
Worksheet - NEC 2008
Customer Name
Customer Address | [6 empty] | email:
Phone
Date | [6 empty] | Fax:
Voltage (Circle) |  | 120/240V- 1Ø |  | 120V/208Y - 3Ø |  |  | 120V/240Δ - 3Ø
Electrical Service (Circle) | 100 Amp |  | 150 Amp | 200 Amp | 400 Amp |  | 600 Amp | 800 Amp
Fuel Type (Circle) |  |  | LPV | NG
Panel Loc/Distance to Gen Loc |  | Garage | Basement | Room | Dist.______________ |  | Ft.
General Loads | Sq.Ft | Qty. | Rating | Factor | Loads (VA) |  |  |  | Loads(VA) kW(VA/1000) |  | Amps
General Lighting | 0 |  | 3.5VA per ft² | 100% | 0 |  |  | 0 |  |  | 0
Small Appliance Circuits |  | 0 | 1500 | 100% | 0 |  |  | 0 |  |  | 0
Laundry Circuits |  | 0 | 1500 | 100% | 0 |  |  | 0 |  |  | 0
Fixed Appliances |  |  | Full Power Rating |  |  |  |  | Gen kW Rating |  |  | Full Current Rating
Well Pump | 240V | 0 | 1000 | 100% | 0 | VA | 1 | 0 | kW | 4.2 | 0 | A
Sump Pump | 120V | 0 | 750 | 100% | 0 |  | 0.75 | 0 |  | 5.5 | 0
Ejector Pump 1 h.p. | 240V | 0 | 2000 | 100% | 0 |  | 2 | 0 |  | 7.5 | 0
Freezer | 120V | 0 | 400 | 100% | 0 |  | 0.4 | 0 |  | 3.3 | 0
Microwave | 120V | 0 | 1000 | 100% | 0 |  | 1 | 0 |  | 8.3 | 0
Toaster Oven | 120V | 0 | 1250 | 100% | 0 |  | 1.25 | 0 |  | 10 | 0
Disposal | 120V | 0 | 250 | 100% | 0 |  | 0.25 | 0 |  | 2 | 0
Dishwasher | 120V | 0 | 500 | 100% | 0 |  | 0.5 | 0 |  | 4.5 | 0
Range (See Table 220.55 for Multiple Cooking App. Or per 8" Element | 240V | 0 | 1500 | 100% | 0 |  | 1.5 | 0 |  | 6.3 | 0
Wall Mounted Oven | 240V | 0 | 5000 | 100% | 0 |  | 5 | 0 |  | 25 | 0
Water Heater (Electric) | 240V | 0 | 4500 | 100% | 0 |  | 4.5 | 0 |  | 18.5 | 0
Clothes Dryer (Electric) | 240V | 0 | 5000 | 100% | 0 |  | 5 | 0 |  | 21 | 0
Furnace/Air Handler | 120V | 0 | 750 | 100% | 0 |  | 0.75 | 0 |  | 7 | 0
Refrigerator | 120V | 0 | 750 | 100% | 0 |  | 0.75 | 0 |  | 6 | 0
Other(s) List |  | 0
0
Total Special Loads |  |  |  |  | 0 | VA |  | 0 | kW |  | 0 | A
Heat / AC Loads
AC Cooling Equipment |  |  | Ton |  |  | Locked-Rotor Amp(LRA) |  | Gen kW Rating |  | Running Load Amp(RLA)
• Compressor 1 | 230V | 0 | 0 | 100% | 0 |  | 0 | 0 |  | 0 | 0 | A
• Compressor 2 | 230V | 0 | 0 | 100% | 0 |  | 0 | 0 |  | 0 | 0
• Heating Element | 230V | 0 |  | 100% |  |  |  | 0
• Heat Pump | 230V | 0 |  | 100% |  |  |  | 0
Electric Space Heating
• Less than 4 separately controlled units |  | 0 | [5 empty] | 0
• 4 or more separately controlled units |  | 0 | [5 empty] | 0
Any Continuous Nameplate Load |  | 0 | [5 empty] | 0
Total AC/Heat Loads |  |  |  |  | 0 | VA |  | 0 | kW |  | 0 | A
General Loads | [9 empty] | Total A | 0 | A
• 1st 10kW of General Loads |  |  |  | 100% | 0 | kW
• Remaining General Loads (kW) |  |  |  | 40% | 0 | kW
Calculated General Loads (kW) | [7 empty] | 0 | kW |  | 0 | A
AC Load |  |  |  | 100% | 0
HeatLoad |  |  |  | 100% | 0
Largest of AC/Heat Load | [7 empty] | 0 | kW |  | 0 | A
Total Calculated Load (Net General Loads + Heat/AC Loads) |  |  |  |  | 0 | VA |  | 0 | kW |  | 0 | A
| Actual Generator size = Total x 10% |  |  |  | 0 | kW |  | 0 | kW | *
*Whole-House: Use as is. |  |  |  |  | 8/7kW = 35amps (28-amp max after adding up items)
*When doing partial-building, look at the amp total (Total A). Than look at |  |  |  |  | 10/9kW = 45amps (36-amp max after adding up items)
the Amp/CB table to the right. This is more accurate due to all the items |  |  |  |  | 14/13kW = 60amps (48-amp max after adding up items)
selected are likely to be on at same time. |  |  |  |  | 17/16kW = 65amps (52-amp max after adding up items)
20/18kW = 100amp (80-amp max after adding up items.
|  |  | Yellow = Entry |  | If used as whole-house, follow sheets recommendation
Use forPartial Building
}

## AC Line-Up
2010 Air-Cooled Line - Up
Model | 5837 | 5870 | 5871 | 5872 | 5874 | 5875
Rated Power (LPG/NG) | 7/6 kW | 8/7 kW | 10/9 kW | 14/13 kW | 17/16 kW | 20/18 kW
Voltage (1Ø) | 120/240 | 120/240 | 120/240 | 120/240 | 120/240 | 120/240
Amps @ (120v/240v) | 58/29 | 58/29 | 63/37.5 | 95/54.2 | 117/66.6 | 133/75
Main Line Circuit Breaker | 30 | 35 | 45 | 60 | 65 | 100
Fuel Consumption (NG) kBTU-Full Load | 146 | 139 | 156 | 220 | 261 | 294
Whisper Test Low Speed | No | No | No | No | No | No
dB(A) @ Exercise | 67 | 62 | 63 | 66 | 66 | 66
dB(A) @ Load | 67 | 62 | 63 | 66 | 60 | 60
ATS (Amp) | 50 | 100 | 100 | 100 | 100 | 200
Circuits Protected | 8 | 10 | 12 | 14 | 14 | Whole-House
Common Electrical Loads | 1) Furnace 2) Sump Pump 3) Refigerator 4) Few lights/TV | 1) Furnace 2) 2-Sump Pumps 3) Refigerator 4) Freezer 5) Few lights/TV | 1) Furnace 2) 2-Sump Pumps 3) Refigerator 4) Freezer 5) AC 3-Ton* 6) Few lights/TV | 1) Furnace 2) 2-Sump Pumps 3) Refigerator 4) Freezer 5) AC 4-Ton or 3-Ton & 2-Ton* 6) Lights/TV | 1) 2-Furnace 2) 2-Sump Pumps 3) 2-Refigerator 4) Freezer 5) AC 5-Ton* or 4-Ton & 2-Ton* 6) Lights/TV | Only up to 200 amp services. No 400A services.
Enclosure Material | Composite Polymer | Steel | Steel | Steel | Aluminum | Aluminum
Enclosure Color | Bisque | Bisque | Bisque | Bisque | Gray | Gray
Dimensions (Inches) | 30.22 x 24.35 x 32.95 | 48.3 x 25.3 x 28.8 | 48.3 x 25.3 x 28.8 | 48.3 x 25.3 x 28.8 | 48.3 x 25.3 x 28.8 | 48.3 x 25.3 x 28.8
Starting Cost | 5800 | 6400 | 7300 | 8100 | 9450 | 10500
* This can vary depending on actual RLA and LRA.
HS Costs (With and without Shipping & Battery)
Generac wo/w | $1636.14/$1851.14 | $2029/$2244 | $2619.60/$2834.60 | $3091.72/$3306.72 | $3717.02/$3932.02 | $4164.72/$4379.72
Standard Installation: | 1. Generator is located within 5' of the Gas Meter.
See prices above. | 2. Generator is within 25' of the Electrical Panel and has a non-interrupted indoor/crawl run.
3. No concrete pad.
4. A 3' area on either side of the Electrical Panel
• Standard Installation consists of clearing the area, installing a 2.5' x 4.5' wood frame set mostly into the ground.
The frame is filled with pea-stone and the unit is set onto the stone.
• 5' of Gas Line run straight from the gas meter with shut-off valve. Line is capped and pressurized for
Plumbing inspection.
• Transfer Switch is installed at electrical panel. The 2' whip is run between the panel and switch and all circuits spliced.
• The 30' whip is run between the Transfer Switch and a Junction Box. A 6' whip is run from JB to Generator.
• Customer or HS calls for Plumbing inspection. After inspection, we make gas connection and perform Start-Up tests.
Non-Standard: | • Generator is located greater than 5' from Gas Meter. This will require additional gas pipe or |  |  |  |  | $6.00 / ft.
CSST tubing:
| • Generator is further than 25' from Electrical or has an obstruction requiring PVC pipe and wire; |  |  |  |  | $3.00 / ft. +
| with possible second day of install if PVC run is long and/or hard |  |  |  |  | $1800 / ft.
| • Concrete Pad required for liquid-cooled generators only: |  |  |  |  | ~$1200
| • Transfer Switches can only be located more than 2' from the Electrical Panel under special, very |  |  |  |  | $ T&M
expensive means.
Procedure: | Site Visit:
• Pictures of gas meter, generator location, panel, and close-ups of same.
• Pictures of the panel label and any pictures of the anticipated electrical and gas line runs.
• Make of panel and breakers.
• List of electrical items to be covered. If AC is considered, get MCA, RLA & LRA.
• If quoted on-site, get survey.
• Load calculation for unit sizing. Quote customer. If accepted, proposal and deposit.
• Design- electrical and plumbing drawings and site survey. Apply for permits and zoning. Allow 1-3 weeks.
• After zoning passes, order unit if not in stock.
• Build wood frame in shop if crew is available. Get wood and stones ready.
• Once permits are ready, schedule job. Job will take 1-2 days for install and 2-3 hours for gas line connection
and start-up.
Generac generators vent from the left side. Any shrubbery within 3-5' of the vent may be killed.

## Site Visit
1. Site
· Recommend the location. Closer to the gas meter is ideal &/or near to the electrical panel
· Unit vents ‘left’. When facing the front of the unit, the vent is on the left side. Do not place the unit within 5’ of a building jut-out, shrubbery, window…
· Will need survey for zoning approval
· See Figure 1.10 Installation Guidelines for placement location
· Unit will sit on 4”of pea-stone inside a 2”x4” wood frame set about 4” into the ground
Pictures: | Site location. Any possible generator locations. Close up and entire area. (2 min.)
2. Plumbing
· Check gas meter & regulator for size
- Primary must supply 5”-14” w.c.
- Secondary regulator is supplied by Generac
· Outside piping is in galvanized steel pipe with a ball valve at the meter & connects to ¾” pipe thread flex-line supplied by Generac
· Inside run is CSST transition at entry and exit with a Brass Transition Flange
· Try to keep all gas line outside if possible. See Diagram in Section2.3 NJNG Outside Locations for Standard Metersets
Pictures: | Close up of entire gas meter. Step back for entire gas line run. Inside CSST run. Any odd obstacles for gas line run. (3 min.)
3. Electrical
· Service size. Main CB, panel make, breaker type. AC nameplate data-MCA, RLA & LRA
· Location of panel-Garage, Basement… Need 3’ of clear area on 1 side of the panel for the transfer switch
· Measure the distance from the transfer switch to generator location from the inside. The 30’ whip will need to reach where it will exit the building and enter a splice box, not to the Generator itself; similar to an AC condensor HR going to the disconnect.
· The 30’whip is not outdoor rated and must be run indoors or crawl. If the unit is within 25’ but there is a slab, doorway or any obstacle, than PVC must be used. The whip can be used and transitioned to PVC when outside or just run PVC the whole way. The wires are THWN-2 and rated for outdoor.
· Obtain basic necessities needed and ‘would like’ from the customers. Fill out Size Form for both kW and Amps
Pictures: | Panel area, close up and set back. Close up of the breakers and panel label(circuits ID). Set Back of conduit run in the room. Service entrance and meter. (4 min.)

## Fuel Usage
Generator Fuel Usage
Based on $1.05/Therm (which includes BGS & Delivery)
In Costs/hr.
Gen Size (kW) | 1/2 Load | Full Load | Exercise
| BTUx1000 = Cost/hr | BTUx1000 = Cost/hr | BTUx1000 = Cost/hr
7 / 6
8 / 7 | 77 = $0.81 | 139 = $1.46 | 30 = $0.32
10 / 9 | 102 = $1.07 | 156 = $1.64 | 35 = $0.37
14 / 13 | 156 = $1.64 | 220 = $2.31 | 40 = $0.42
17 / 16 | 183 = $1.92 | 261 = $2.74 | 45 = $0.47
20 / 18 | 206 = $2.16 | 294 = $3.09 | 50 = $0.53
Load At→ | 25% | 50% | 75% | 100% | Exercise
22kW | 100 = $1.10 | 190 = $2.00 | 255 = $2.68 | 316 = $3.32 | 42 = $0.44
36/35kW | 156 = $1.64 | 282 = $2.96 | 392 = $4.12 | 503 = $5.28 | 48 = $0.50
1 Therm = 100ft3 = 100,000 BTU
1 T = | 100 ft3 | (y/100) x ($ / Therm) = $ / hr.
x T = | y ft3