## Sheet1
Voltage Drop Calculation
National Electrical Code
Per Section 210-19 (A) (1) FPN (4)
Introduction:
Calculating voltage drop for feeder conductors: (3 phase, 4 Wire Systems)
|  |  |  | Voltage Drop = |  | (2K) (Wire Length) (Demand Amps) | [7 empty] | X | 0.866
Wire Circular Mil Area
|  |  |  | K = | 12.9 Ohms-CMA / Ft. (for Copper Wire)
|  |  |  | K = | 21.2 Ohms-CMA / Ft. (for Aluminum Wire)
The following calculated Voltage Drop with the following data:
| K | = | 12.9 | Wire Length | = | 300 |  | Demand Amps |  |  |  | = | 180
|  |  |  | Wire Circular Mills | = | 167800 |  | X | 1 | = | 167800
|  |  |  | Allowable Voltage Drop | = | 3 |  | Supply Voltage |  |  |  | = | 240
Calculation:
|  |  |  | Voltage Drop = | 2 | X | 12.9 | X | 300 | X | 180 | = | 1393200 | = | 8.3027
[5 empty] | 167800 | [7 empty] | 167800
[5 empty] | 8.3027 |  | x | 0.866 |  | = | 7.1902 | Volts
The following calculated Allowable Voltage Drop with the following data:
|  |  | Allowable Voltage Drop |  | = | Supply Voltage X Allowable Voltage Drop
|  |  |  | Supply Vollatge | = | 240 | Allowable Voltage Drop |  |  |  |  | = | 3
Calculation:
|  |  |  | Allowable Voltage Drop = | 240 |  | X | 0.03 |  | = | 7.2 | Volts
|  |  |  | Voltage Drop = | 8.3027 |  | ÷ | 240 |  | = | 0.034595 | Volts

## Sheet2
Wire Properties
Wire | Circular | THHN
size | mils | Area
18 | 1620
16 | 2580
14 | 4110 | 0.0097
12 | 6530 | 0.0133
10 | 10380 | 0.0211
8 | 16510 | 0.0366
6 | 26240 | 0.0507
4 | 41740 | 0.0824
3 | 52620 | 0.0973
2 | 66360 | 0.1158
1 | 83690 | 0.1562
1/0 | 105600 | 0.1855
2/0 | 133100 | 0.2223
3/0 | 167800 | 0.2679
4/0 | 211600 | 0.3237
250 | 250000 | 0.397
300 | 300000 | 0.4608
350 | 350000 | 0.5242
400 | 400000 | 0.5863
500 | 500000 | 0.7073
600 | 600000 | 0.8676
700 | 700000 | 0.9887
750 | 750000 | 1.0496
800 | 800000 | 1.1085
900 | 900000 | 1.2311
1000 | 1000000 | 1.3478
1250 | 1250000
1500 | 1500000
1750 | 1750000
2000 | 2000000